Surname: ………………………………...….

First Name: ……………………………….....

I.D./P.P.Nο: …….…………………………...

Candidate Nο: ………………………..….….

REPUBLIC OF CYPRUS

MINISTRY OF COMMUNICATIONS & WORK

DEPARTMENT OF ELECTROMECHANICAL SERVICES

Electricity Regulations 1941 - 2004

EXAMINATION PARER

ELECTRICAL EQUIPMENT MAINTAINERS - GRADE Β´

LEFKOSIA

May 2009

| 1. | According to the provisions of the Electricity Regulations, the emergency switch of a circuit supplying an electrical machine should be placed at a distance from the machine: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | Of less than 2,5m from the machine |  |  |
|  | (b) | Equal to 2,5m from the machine |  |  |
|  | (c) | Of less than 3m from the machine |  |  |
|  | (d) | Of less than 2m from the machine |  | √ |
| 2. | The maximum allowable starting current of 26A (full load current) electric motor is: |  |  |  |
|  | (a) | 26A |  |  |
|  | (b) | 78A |  |  |
|  | (c) | 39A |  | √ |
|  | (d) | 52A |  |  |
| 3. | A possible cause of overheating of a star connected three-phase electric motor is: |  |  |  |
|  | (a) | Operation with one phase |  |  |
|  | (b) | Faulty starting capacitor |  |  |
|  | (c) | Operation with two phases |  | √ |
|  | (d) | Operation with the neutral short circuited with earth |  |  |

| 4. | If a metal object, brings in contract the live conductors of an electric motor, will cause: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | Overspeed of the motor |  |  |
|  | (b) | Fault to the earth and short-circuit |  |  |
|  | (c) | Short – circuit |  | √ |
|  | (d) | Fault to the earth |  |  |
| 5. | In case of replacement of a 30A/220V/6KA miniature circuit breaker (MCB), which one of the following options should be selected? |  |  |  |
|  | (a) | 32Α/220V/3KA |  |  |
|  | (b) | 30Α/440V/3KA |  |  |
|  | (c) | 20Α/230V/6KA |  |  |
|  | (d) | 32Α/250V/9KA |  | √ |
| 6. | The running current of a split type air conditioning unit is 14A. The most suitable miniature circuit breaker (MCB) for the protection of the circuit is: |  |  |  |
|  | (a) | 20A, type C |  | √ |
|  | (b) | 16A, type B |  |  |
|  | (c) | 32A, type B |  |  |
|  | (d) | 20A, type D |  |  |

| 7. | For a considerable reduction of the running current of an electric motor, the maintainer may suggest: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | Reduction of the load |  |  |
|  | (b) | Improvement of the supply voltage |  |  |
|  | (c) | Power factor correction |  | √ |
|  | (d) | Improvement of the efficiency |  |  |
| 8. | A type B miniature circuit breaker should trip within the time specified in the relevant standard for currents: |  |  |  |
|  | (a) | 10 - 50 times the nominal current (In) |  |  |
|  | (b) | 5 - 10 times the nominal current (In) |  |  |
|  | (c) | 3 - 5 times the nominal current (In) |  | √ |
|  | (d) | 2 - 4 times the nominal current (In) |  |  |
| 9. | The full load current of a single phase load with nominal power 2346W and cos φ 0,85 supplied with 230V, is: |  |  |  |
|  | (a) | 10,2A |  |  |
|  | (b) | 8,7A |  |  |
|  | (c) | 12,5A |  |  |
|  | (d) | 12A |  | √ |

| 10. | Which one of the following values is the largest? |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | 0,1KΩ |  |  |
|  | (b) | 150Ω |  |  |
|  | (c) | 0,001ΜΩ |  |  |
|  | (d) | 1,1ΚΩ |  | √ |
| 11. | A miniature circuit breaker (MCB) was destroyed due to a short – circuit fault between line and neutral. The reason is that the MCB´s: |  |  |  |
|  | (a) | Rated current (A) is low |  |  |
|  | (b) | Type is not suitable for the purpose |  |  |
|  | (c) | Breaking capacity (KA) is low |  | √ |
|  | (d) | Rated current (A) is high |  |  |
| 12. | The auxiliary winding of a single phase induction motor is essential for: |  |  |  |
|  | (a) | The starting of the motor |  | √ |
|  | (b) | Improvement of power factor |  |  |
|  | (c) | Limiting overload and short-circuit currents |  |  |
|  | (d) | The stabilizing of the running current of the motor |  |  |

| 13. | A short - circuit between line and neutral of an electric motor, will cause the tripping of: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | The thermal overload switch of the motor |  |  |
|  | (b) | The Residual Current Device (RCD) of the installation |  |  |
|  | (c) | The miniature circuit breaker (MCB) of the circuit and the thermal overload switch of the motor |  |  |
|  | (d) | The miniature circuit breaker (MCB) of the circuit |  | √ |
| 14. | Undervoltage protection is needed where loss and subsequent restoration of voltage may cause the, |  |  |  |
|  | (a) | Unexpected operation of the protective devices |  |  |
|  | (b) | Burning out of lamps |  |  |
|  | (c) | Unexpected restarting of machinery |  | √ |
|  | (d) | Malfunction of magnetic devices |  |  |
| 15. | When an emergency switch is released, |  |  |  |
|  | (a) | The electrical machine should be re-energized |  |  |
|  | (b) | The electrical machine should not be re - energized |  | √ |
|  | (c) | The overload protection will operate |  |  |
|  | (d) | The fault warning light will indicate a fault on the circuit |  |  |

| 16. | A Starter incorporating overcurrent protection must be provided for every electric motor having a power rating exceeding |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | 0,5 KW |  |  |
|  | (b) | 0,37 KW |  | √ |
|  | (c) | 0,6 KW |  |  |
|  | (d) | 1,0 KW |  |  |
| 17. | A water pump is marked with “IP 44”. This marking denotes: |  |  |  |
|  | (a) | The first digit is the degree of dust protection and the second, the degree of moisture protection |  | √ |
|  | (b) | The class for shock protection |  |  |
|  | (c) | The first digit is the degree of moisture protection and the second, the degree of dust protection |  |  |
|  | (d) | The first digit is the class of shock protection and the second, the number of isolator poles. |  |  |
| 18. | A single phase induction motor consists of: |  |  |  |
|  | (a) | Three windings and a starting capacitor |  |  |
|  | (b) | One winding and a starting capacitor |  |  |
|  | (c) | Two windings and a power factor correction capacitor |  |  |
|  | (d) | Two windings and a starting capacitor |  | √ |

| 19. | The primary and secondary voltages of a transformer are 100V and 10V respectively. If the primary current is 6A, the secondary current is: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | 0,6 Α |  |  |
|  | (b) | 36 Α |  |  |
|  | (c) | 60 Α |  | √ |
|  | (d) | 10 Α |  |  |
| 20. | The resistance of each one of the windings of a 25HP, 400V three phase electric motor, is expected to be: |  |  |  |
|  | (a) | Less than 50Ω |  |  |
|  | (b) | Between 50 and 100Ω |  |  |
|  | (c) | Less than 5Ω |  | √ |
|  | (d) | Greater than 1MΩ |  |  |
| 21. | Class II insulation, of an equipment: |  |  |  |
|  | (a) | Offers protection against indirect contact only |  |  |
|  | (b) | Offers protection against direct and indirect contact |  |  |
|  | (c) | Does not offer protection against direct and indirect contact |  |  |
|  | (d) | Offers protection against direct contact only |  | √ |

| 22. | To ensure compliance of an electrical installations with the provisions of the Regulations, as far as protection against damage, deterioration or defects, is concerned: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | The owner of the installation should have a basic knowledge of the Regulations and the use of testing instruments |  |  |
|  | (b) | Every installation should be inspected and tested at regular intervals |  | √ |
|  | (c) | The owners of the installation should have a basic knowledge of the Regulations |  |  |
|  | (d) | The contractor should test all installations executed by himself, at least once every three years. |  |  |
| 23. | According to the General Terms for the Electrical supply of the Electricity Authority of Cyprus (E.A.C.) the lowest acceptable value of power factor (lagging) is: |  |  |  |
|  | (a) | 0,9 |  |  |
|  | (b) | 0,95 |  |  |
|  | (c) | 0,85 |  | √ |
|  | (d) | 0,8 |  |  |
| 24. | Which one of the following appliances is NOT considered to have low power factor? |  |  |  |
|  | (a) | Welding machine |  |  |
|  | (b) | Fluorescent luminaire |  |  |
|  | (c) | Discharge luminaire |  |  |
|  | (d) | Electrical resistance oven |  | √ |

| 25. | The isolator of a three phase air – conditioning unit, supplied from a TN-C-S system, must isolate: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | The three phases |  | √ |
|  | (b) | The three phases, neutral and earth |  |  |
|  | (c) | The three phases and neutral |  |  |
|  | (d) | The three phases and earth |  |  |
| 26. | Which one of the following conditions may give rise to a risk of “Direct Contact”? |  |  |  |
|  | (a) | A 13A plug with a broken cover |  | √ |
|  | (b) | A metal bulkhead fitting which is secure, but ineffectively earthed |  |  |
|  | (c) | A difference in ground potential adjacent to an earth electrode |  |  |
|  | (d) | A steel conduit installation in which couplings and bushes are left lose |  |  |
| 27. | Where an installation incorporates a Residual Current Device (RCD), the label at the origin of the installation must indicate that the RCD should be tested: |  |  |  |
|  | (a) | Quarterly |  | √ |
|  | (b) | Half – yearly |  |  |
|  | (c) | Annually |  |  |
|  | (d) | Bi - annually |  |  |

| 28. | Operating the RCD´S integral test button will verify: |  |  |  |
| --- | --- | --- | --- | --- |
|  | (a) | The continuity of the main earthing conductor |  |  |
|  | (b) | The effectiveness of the earth electrode |  |  |
|  | (c) | The continuity of final circuit protective conductors |  |  |
|  | (d) | The functionality of the internal mechanism of the device |  | √ |
| 29. | Which one of the following may be used to provide emergency switching for an electric machine? |  |  |  |
|  | (a) | A key-switch latched in the ON position |  |  |
|  | (b) | A plug and socket outlet |  |  |
|  | (c) | A switch-fuse with a removable handle |  |  |
|  | (d) | A device which latches in the OFF position |  | √ |
| 30. | Suitable precautions shall be taken where either a reduction in voltage or a loss and subsequent restoration of voltage: |  |  |  |
|  | (a) | Are routine events |  |  |
|  | (b) | Could cause danger |  | √ |
|  | (c) | Occur infrequently |  |  |
|  | (d) | Will not cause danger |  |  |